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(2026Aug FireSeal.docx)
RECOMMENDED ENGINEERING SPECIFICATION FOR AssureFlex® FIRESEAL BELLOWS™
PIPE FLOOR/WALL PENETRATION BELLOWS SEAL

PART 1 GENERAL

1.01	SECTION INCLUDES

A. AssureFlex FireSeal Bellows pipe penetration sealing system consisting of a flexible 300 series stainless steel bellows element extending around a penetrating pipe at a floor or wall opening. The bellows shall accommodate axial movement of the penetrating pipe while maintaining the firestop system.
a. Provide the appropriate seismic or non-seismic model for the application. Seismic models shall provide clearance around the penetrating pipe in accordance with NFPA 13 recommendations.
b. Provide end fittings suitable for attachment to the mating piping. End fittings may be carbon steel, 304 stainless steel, or 316 stainless steel, as specified.
c. Provide the appropriate nominal size from 2 inches through 12 inches.


1.02	MANUFACTURER

A.  Provide the appropriate AssureFlex FireSeal Bellows pipe penetration sealing system as manufactured by Flex-Hose Co., or approved equal.

PART 2 PRODUCTS

2.01 Pipe Floor/Wall Penetration Bellows Seal

1. FireSeal Bellows assemblies shall be made in the USA.
1. Bellows element shall be 300 series stainless steel.
1. End fittings shall be carbon steel, 304 stainless steel, or 316 stainless steel, as specified for the mating piping.
1. Base plate shall be carbon steel as standard. A 300 series stainless steel base plate shall be available as an option.
1. Protective shroud shall be 300 series stainless steel and shall surround the bellows element to provide mechanical protection.
1. The base plate shall be configured to attach to the floor or wall surrounding the pipe penetration.
1. The flexible bellows shall accommodate axial expansion and contraction of the penetrating pipe while maintaining the fire seal.
1. Seismic models shall provide clearance around the penetrating pipe in accordance with NFPA 13 recommendations. FireSeal Bellows shall be UL 1479 listed for penetration firestop applications.
1. Fire-rated sealant shall be applied between the base plate and penetrating surface in accordance with the manufacturer's installation instructions. 3M™ CP 25WB+ fire-rated sealant is specified in the current installation instructions.
1. The mating piping shall be independently supported so the FireSeal Bellows assembly does not carry the load of the piping system.
1. The assembly shall require no routine maintenance other than periodic inspection for external damage and repainting of carbon steel surfaces as required.
1. Product shall be covered by U.S. Patent No. 11,221,075 B2.
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