(2023Apr_BrzPC.docx)

# RECOMMENDED ENGINEERING SPECIFICATION FOR PumpSaver™

# BRONZE BRAIDED METAL PUMP CONNECTOR (for COPPER TUBING)

## PART 1 GENERAL

1.01	SECTION INCLUDES

- PumpSaver braided metal pump connector(s). Provide appropriate  model braided metal pump connector(s)  to connect to mating pipe/tubing:

  - Model BSW copper female sweat ends

  - Model BMN carbon steel male NPT ends

  - Model BPP/Q-Press copper female press style ends

1.02	MANUFACTURER

A.  PumpSaver braided metal pump connector shall be manufactured by Flex-Hose Co. or pre-approved equal.

PART 2 PRODUCTS

2.01 Braided metal pump connector(s)

## The hose shall be copper alloy C51000 (95/5) annular corrugated (manufactured in the USA).

- The braid shall commercial bronze C22000 (90/10) (manufactured in the USA).

- The copper ring ferrule or band shall be of not less than 0.032” thick material.

- The hose, braid and ferrule shall be integrally seal-welded using a 100% circumferential TIG weld.

- All end fittings shall be must be attached using 100% circumferential TIG weld.

- Braided bronze pump connector must be suitable for operating temperatures up to 400 degrees F (204° C).

- The rated working pressure of the hose must have a 4:1 safety factor.

- Each braided metal hose pump connector is to be individually leak tested by the manufacturer using air-under-water, helium leak detection and/or hydrostatic pressure.

- Model BSW shall be supplied with copper female sweat ends.

## Model BMN shall be supplied with carbon steel schedule 40 male NPT ends.

- Model BPP/Q-Press shall be supplied with copper female press type ends.

## For the Canadian market they must be CSA standard B51 certified, inspected, and tested by the Technical Standards and Safety Authority of Canada.

- When used for potable water the model BSW and BPP shall be third party tested and, listed (by a laboratory in compliance with all applicable requirements of ISO/IEC 17025) and marked in accordance with NSF/ANSI 61-2020

- When used for potable water the model BSW and BPP shall be third party tested and, listed (by a laboratory in compliance with all applicable requirements of ISO/IEC 17025) and marked in accordance with Section 1417(d) of the Safe Drinking Water Act. Must meet the lead content requirements of Section 116875 of the California Health & Safety Code, and the criteria of NSF/ANSI 372 for low lead.

Special Note: Drinking water supplies that are less than pH 6.5 may require corrosion control to limit leaching of copper into the drinking water.

  - WARRANTY

PumpSaver model bronze braided metal pump connector(s) must have a 3-year full product replacement warranty when installed in accordance with all specifications and installation instructions as described by Flex-Hose Co.