(2023Apr_Hngr.docx)

# RECOMMENDED ENGINEERING SPECIFICATION FOR HANGER ASSEMBLY KIT

## PART 1 GENERAL

1.01	SECTION INCLUDES

- UL Listed Seismic Wire Rope/Cable™ for installation of Tri-Flex Loop(s)® and Tri-Loop(s)® flexible pipe loops.

1.02	MANUFACTURER

A.  Utilize UL Listed Wire/Rope Cable kits, for installation of all Tri-Flex Loops or Tri-Loops, as supplied by Flex-Hose Co, or approved equal.

PART 2 PRODUCTS

2.01 Hanger Assembly Kit

- The wire/rope cable shall conform to the requirements of the ACSE (American Society of Civil Engineers) guidelines for structured applications of wire rope.

- The cable used in the kit shall be pre-stretched and break-strength certified.

- The cable(s) will be color coded throughout its entire length.

- End fittings shall be permanently attached and maintain a safety factor of 2:1.

- One kit is required for installation of each Tri-Flex Loop

- Use gold color coded kit for installation of Tri-Flex Loops up to and including 8” nominal pipe size.

- Use green color coded kit for installation of Tri-Flex Loops 10” & 12” nominal pipe size.

- The kit shall include the following:

  - Two color coded cables, each 14 feet in length.

  - Two URC (Universal Restraint Clips) for attaching to structure

  - Eight (4 are extra) zinc plated copper oval sleeves

- Installation shall be made performed utilizing the manufacturer’s instructions contained with each kit supplied.