# (2023Apr PurgAir.docx)

# RECOMMENDED ENGINEERING SPECIFICATION FOR PurgAir® INLINE AIR SEPARATOR

## PART 1 GENERAL

1.01	SECTION INCLUDES

- PurgAir model inline air separator(s) available in sizes 3” through 18” nominal pipe size

  - Model PurgAir FF has 150# plate carbon steel fixed flanges

  - Model PurgAir GG has schedule 40 / standard weight carbon steel groove ends

  - Model PurgAir WW has carbon steel schedule 40 / standard weight weld ends

1.02	MANUFACTURER

A.  PurgAir model inline air separator shall be provided by Flex-Hose Co. or pre-approved equal.

PART 2 PRODUCTS

2.01 Furnish and install PurgAir model inline air separator

- Select and provide the proper model based on mating piping.

- The body shall be manufactured from carbon steel standard weight pipe.

- Standard pressure design rating of 150 PSI

- Flanged units are to be supplied with carbon steel plate fixed flanges ( 150# ANSI OD and drilling)

- The centerline of the upper vent coupling and the lower drain coupling are to straddle the flange bolt holes centerlines,, to allow vertical alignment with other piping components

- All welding to be performed in accordance with section IX of the ASME pressure vessel code.

- Each unit to be individually leak tested at factory,  prior to shipment