(2023Apr SSPC.docx)

# RECOMMENDED ENGINEERING SPECIFICATION FOR PumpSaver™

# BRAIDED METAL PUMP CONNECTOR (for steel piping)

## PART 1 GENERAL

1.01	SECTION INCLUDES

- PumpSaver braided metal pump connector(s). Provide appropriate model braided metal pump connector(s)  to connect to mating piping:

  - Model SMP 150# carbon steel plate flanges

  - Model SMN carbon steel male NPT ends

  - Model SVG carbon steel grooved pipe ends

  - Model SF/CI-15P 150# carbon steel plate reducing ends

  - Model SFCI-15PxVG carbon steel plate flange x grove end reducing ends

1.02	MANUFACTURER

A.  PumpSaver braided metal pump connector shall be manufactured by Flex-Hose Co. or pre-approved equal.

PART 2 PRODUCTS

2.01 Braided metal pump connector(s)

## The hose shall be 321/304L annular corrugated stainless steel (manufactured in the USA).

- The braid shall be 304 stainless steel (manufactured in the USA).

- The stainless steel ring ferrule or band shall be of not less than 0.048” thick material.

- The hose, braid and ferrule shall be integrally seal-welded using a 100% circumferential TIG weld.

- The hose shall have the first “lip” removed (on flanged models) to insure there are no sharp edges.

- All end fittings shall be must be attached using 100% circumferential weld.

- Braided stainless steel pump connectors must be suitable for operating temperatures up to 850 degrees F (455° C).

- The rated working pressure of the hose must have a 4:1 safety factor.

- Each braided metal hose pump connector is to be individually leak tested by the manufacturer using air-under-water, helium leak detection, and/or hydrostatic pressure.

- Model SMP shall be supplied with flat-face carbon steel plate flanges with drilling and outside diameter to 150# ANSI.

## Model SMN shall be supplied with carbon steel schedule 40 male NPT ends.

## Model SVG shall be supplied with carbon steel schedule 40 groove pipe ends.

- Model SF/CI-15P shall be supplied with the smaller ID plate flange welded to a carbon steel schedule 40 concentric reducer.  The corrugated metal hose inside diameter shall match the nominal size of the larger flange to minimize media pressure drop.

- Model SF/CI-15pxVG shall be supplied with the smaller ID plate flange welded to a carbon steel schedule 40 concentric reducer.  The corrugated metal hose inside diameter shall match the nominal size of the larger groove end diameter to minimize media pressure drop.

- Flanged end pump connectors shall be prepared for shipment using cut-to-length spacers, securely positioned between the flanges to prevent axial compression damage during shipment and to maintain the manufactured length.

- For the Canadian market they must be CSA standard B51 certified, inspected and tested by the Technical Standards and Safety Authority of Canada.

- When used for potable water the models SMP, SMN and SVG shall be third party tested and, listed (by a laboratory in compliance with all applicable requirements of ISO/IEC 17025)  and  marked  in accordance with NSF/ANSI 61-2011

- When used for potable water the models SMP, SMN and SVG shall be third party tested and, listed (by a laboratory in compliance with all applicable requirements of ISO/IEC 17025) and marked in accordance with Section 1417(d) of the Safe Drinking Water Act. Must meet the lead content requirements of Section 116875 of the California Health & Safety Code, and the criteria of NSF/ANSI 372 for low lead.

  - WARRANTY

PumpSaver model braided metal pump connector(s) must have a 3-year full product replacement warranty when installed in accordance with all specifications and installation instructions as described by Flex-Hose Co.