(2023Apr UFF Spec.docx)

# RECOMMENDED ENGINEERING SPECIFICATION FOR UltraFuel Flex™

# BRAIDED METAL PUMP CONNECTOR

## PART 1 GENERAL

1.01	SECTION INCLUDES

- UltraFuel Flex UL 536 listed braided metal connector(s) for compressed and flammable gases. Provide appropriate model UltraFuel Flex braided metal connector(s) to connect to mating piping:

  - Model UFFMP-UL 150# carbon steel plate flanges

  - Model UFFMN-UL carbon steel male NPT ends

  - Model UFFWN-UL carbon steel beveled pipe ends

  - Model UFFRR-UL 150# raised face forged steel flanges.

  - Model UFFRY-UL 150# raised face forged steel fixed flange x 150# forged steel lap joint floating flange.

1.02	MANUFACTURER

A.  UltraFuel Flex braided metal pump connector shall be manufactured by Flex-Hose Co. or pre-approved equal.

PART 2 PRODUCTS

2.01 Braided metal pump connector(s)

## The assembly shall be listed by UL (Underwriters Laboratories) to standard UL-536 for compressed and combustible gases at a maximum working pressure of 175 PSI at 70 degrees F.  Based on a 5:1 burst to working pressure safety factor.

## The hose shall be 321/304L annular corrugated stainless steel (manufactured in the USA).

- The braid shall be 304 stainless steel (manufactured in the USA).

- The stainless steel ring ferrule or band shall be of not less than 0.048” thick material.

- The hose, braid and ferrule shall be integrally seal-welded using a 100% circumferential TIG weld.

- The hose shall have the first “lip” removed (on flanged models) to insure there are no sharp edges.

- All end fittings shall be must be attached using 100% circumferential weld.

- UL-536 Listed braided stainless steel connectors must be suitable for 175 operating temperatures 70 degrees F (21.1° C).

- The rated working pressure of the hose must have a 5:1 safety factor.

- Each braided metal hose pump connector is to be individually leak tested by the manufacturer using air-under-water.  Upon completion they shall be individually hydrostatically tested to 262.5 PSI (1.5 times rated working pressure).

- Model UFFMP shall be supplied with flat-face carbon steel plate flanges with drilling and outside diameter to 150# ANSI.

## Model UFFMN shall be supplied with carbon steel schedule 40 (minimum) male NPT ends.

## Model UFFWN shall be supplied with carbon steel schedule 40 (minimum) beveled pipe weld ends.

- Model UFFRR shall be supplied with 150# raised face forged steel fixed flanges.

- Model UFFRY shall be supplied with 150# raised face forged steel fixed flange one end and a 150# lap joint forged steel flange floating on a schedule 40 (minimum) type A stub end.

- Flanged end connectors shall be prepared for shipment using cut-to-length spacers, securely positioned between the flanges to prevent axial compression damage during shipment and to maintain the manufactured length.

  - WARRANTY

UltraFuel Flex model braided metal connector(s) must have a 3-year full product replacement warranty when installed in accordance with all specifications and installation instructions as described by Flex-Hose Co.