# (2023Aug MPXJ.docx)

# RECOMMENDED ENGINEERING SPECIFICATION FOR BELLOWSFLEX MULTI-PLY METAL EXPANSION JOINT

## PART 1 GENERAL

1.01	SECTION INCLUDES

- BellowsFlex multi-ply stainless steel bellows expansion joint. Provide appropriate  model multi-ply bellows expansion joint for attachment to mating piping

  - Model BellowsFlex BF/150-FxF*MP* (150# carbon steel plate flange – 150 PSI working pressure)

  - Model BellowsFlex BF/150-WxW*MP* (carbon steel weld ends – 150 PSI working pressure)

1.02	MANUFACTURER

A.  Provide appropriate model multi-ply bellows expansion joint as manufactured by Flex-Hose Co., or approved equal.

PART 2 PRODUCTS

2.01 Metal expansion joints(s)

## Expansion joints shall be made in the USA.

- Bellows element shall be a multiple plies of stainless steel material

- Flanged units shall have 150# carbon steel plate fixed flanges (ANSI OD and drilling)

- Weld end units shall be a carbon steel schedule 40/standard wall pipe (minimum)

- The rated working pressure of the bellows shall have a minimum 3:1 safety factor as per EJMA (Expansion Joint Manufacturers Association)

- Optional tie rods are to be utilized in applications where over-extension of the expansion joint may occur.

- Optional compression stops are to be utilized in applications where over-compression of the expansion joint may occur.

- Where tie rods are require the flanges must be configured with three (minimum) tie rods equally spaced, to prevent over travel and react to thrust loads resulting from internal pressure.

- For the Canadian market they must be CSA standard B51 certified, inspected and tested by the Technical Standards & Safety Authority of Canada with a 4:1 safety factor per EJMA