(2024Nov AFPC.docx)

# RECOMMENDED ENGINEERING SPECIFICATION FOR ASSUREFLEX®

# BRAIDED METAL PUMP CONNECTOR For fire protection systems

## PART 1 GENERAL

1.01	SECTION INCLUDES

- PumpSaver braided metal pump connector(s). Provide appropriate model braided metal pump connector(s)  to connect to mating piping:

  - Model FPSMP 150# carbon steel plate flanges

  - Model FPSMN carbon steel male NPT ends

  - Model FPSVG carbon steel grooved pipe ends

  - Model FPSWN carbon steel weld

  - Model FPSVGXF carbon steel groove end x flange end

  - Model FPSVGCI Carbon Steel concentric reducing groove end

1.02	MANUFACTURER

A.  AssureFlex® braided metal pump connector shall be manufactured by Flex-Hose Co. or pre-approved equal.

PART 2 PRODUCTS

2.01 Braided metal pump connector(s)

## The hose shall be 321/304L annular corrugated stainless steel (manufactured in the USA).

- The braid shall be 304 stainless steel (manufactured in the USA).

- The stainless steel ring ferrule or band shall be of not less than 0.048” thick material.

- The hose, braid and ferrule shall be integrally seal-welded using a 100% circumferential TIG weld.

- The hose shall have the first “lip” removed (on flanged models) to insure there are no sharp edges.

- All end fittings shall be must be attached using 100% circumferential weld.

- Braided stainless steel pump connectors must be suitable for operating temperatures up to 850 degrees F (455° C).

- The rated working pressure of the hose must have a 4:1 safety factor.

- Each braided metal hose pump connector is to be individually leak tested by the manufacturer using air-under-water and/or hydrostatically to 1.5 times rated working pressure prior to shipment.

- Model FPSMP shall be supplied with flat-face carbon steel plate flanges with drilling and outside diameter to 150# ANSI.

## Model FPSMN shall be supplied with carbon steel schedule 40 male NPT ends.

## Model FPSVG shall be supplied with carbon steel schedule 40 groove pipe ends.

## Model FPSWN shall be supplied with carbon steel schedule 40 beveled weld ends.

- Model FPSVGXF shall be supplied with carbon steel schedule 40 grooved end on one end and a 150# carbon steel plate flange on the other end.

- Model FPSVGCI shall be supplied with carbon steel schedule 40 groove ends, one end to include schedule 40 concentric reducer.

- Flanged end pump connectors shall be prepared for shipment using cut-to-length spacers, securely positioned between the flanges to prevent axial compression damage during shipment and to maintain the manufactured length.

- Connectors shall be third party listed by UL (Underwriters Laboratories) for use in fire protection systems in both United States and Canada

- All standard models that are UL listed must be rated for 300 PSI ½”-3” and 175 PSI for sizes 4”-12” nominal hose inside diameter.

- High Pressure models UL listed for 300 PSI 4”-6” nominal hose inside diameters to be used for where pressure indicates.

- For the Canadian market they must be standard B51 certified, inspected and tested by the Technical Standards and Safety Authority of Canada

  - WARRANTY

AssureFlex® model braided metal pump connector(s) must have a 3-year full product replacement warranty when installed in accordance with all specifications and installation instructions as described by Flex-Hose Co.